## INTRO
COPYRIGHT©: 1996-2010 HANS DRESLER + THERMAFLEX ; made by: HANS DRESLER
QUICK CALC AB - (BA)
V. 8.00 - BETA
PIPESIZING A-B(-B-A) for MICROSOFT EXCEL Ver. 97 or higher. This Calculation is based on the Material Properties of "FLEXALEN600". COPYRIGHT©: 1999-2010 HANS DRESLER + THERMAFLEX ; Program made by: HANS DRESLER PIPESIZING A-B(-B-A) for MICROSOFT EXCEL Ver. 97 or higher. This Calculation is based on the Material Properties of "FLEXALEN600".
This Software belongs to THERMAFLEX and must not be copied or transfered to another user without prior approval of Thermaflex. Please note that despite careful development and stringent tests no software can give a guarantee for total faultless results.
If you have any problem please contact the CoE Flexalen: coe-flexalen@thermaflex.com
THERMAFLEX and Mr. Dresler cannot accept any liability for the results or problems with the data or computer. The compatibility of this Software has to be checked by the user prior to the installation.
Please check every result to be safe!

## CALC
(C) 1999-2010 DRESLER + THERMAFLEX / Unautorized passing on of the software is forbidden! | [10 empty] | LANGUAGE
ENGLISH
| PIPE SIZING FOR SINGLE OR DOUBLE LINES BETWEEN 2 NET POSITIONS | [9 empty] | GERMAN
| FLEXALEN 600 - PREINSULATED PIPE SYSTEMS | [9 empty] | BULAGRIAN
| MADE FOR DOMESTIC WATER DISTRIBUTION AND DISTRICT HEATING SUPPLY LINES | [9 empty] | DUTCH
FRENCH
ROMANIAN
| QUALITY FACTOR | 1.83 |  |  | USABLE TEMP. DIFF. |  | not appliable |  |  |  | TURKISH
| TEMPERATUR FACTOR | 1.03 |  |  | USABLE LOAD |  | not appliable |  |  |  | RUSSIAN
| SIZE TUNING | 1 |  |  | NET VOLUME |  | 0
| FLOW TEMPERATURE (Tf) | 0
| RETURN TEMPERATURE (Tr) | 0 |  |  | SOURCE | 0 | RESERVE PRESSURE FOR PUMP
| TEMP. DIFFERENCE (Tf - Tr) | 0 |  |  | TEMP. DIFF. |  | Temperature °C | Pressure loss bar | Dimension OD | END POINT
| TRENCH LENGTH | 0 |  |  | NO
| HEAT LOAD kW SOURCE | 0 | 0 |  |  | FLOW | 0 | 0 | 16
| VOLUMETRIC FLOW RATE | 0 |  |  | PUMP | 0 |  |  | #DIV/0!
| PIPE LENGTH | 0 |  |  | 0 | RETURN | 0 | 0 | not appliable
[5 empty] | 0 | not appliable |  |  | not appliable
| OD (DIMENSION) | 16 |  |  |  |  | 0
| VELOCITY | 0
| PRESSURE DROP FLOW | 0 |  |  | Soil temperature | 10 |  | Temperature drop Flow |  | #DIV/0!
| PRESSURE DROP RETURN | 0 |  |  | Coverage | 800 |  | Trench Length |  | 0
| PRESSURE DROP TOTAL | 0 |  |  | Lambda soil | 1 |  | Dwell time Flow |  | #DIV/0!
| PLEASE CHOOSE APPLICATION: |  | SUPPLY LINE → |  |  | Pressure rating | 8 | at 95°C
[6 empty] | max. Pressure | 16 | at Service Temperature
|  |  | HEATING / COOLING → |  |  | Pressure drop | 0 | FLEXALEN pipes only
[6 empty] | Reserve press. | 16 | at Service Temperature
| FLOW TEMPERATURE |  |  | °C |  | D
| RETURN TEMPERATURE |  |  | °C |  |  | HEATING / COOLING (F / R)
| TRENCH LENGTH |  |  | m
| HEAT LOAD |  |  | kW
| ADDITIONAL PRESSURE FOR PUMP |  |  | bar |  |  |  |  | LANGUAGE: | ENGLISH
Note on C10: This Factor is used to adopt the pipe size. In general it is set to 1. Changing the factor in the range of 0,3 < 1 < 3 will give different dimensions in the calculation.
Note on F17: Pump pressure - pressure drop of Flexalen pipework and reserve pressure e.g. for heat exchanger.
O
OO

## PRINTOUT
PIPE SIZING FOR SINGLE OR DOUBLE LINES BETWEEN 2 NET POSITIONS
FLEXALEN 600 - PREINSULATED PIPE SYSTEMS
MADE FOR DOMESTIC WATER DISTRIBUTION AND DISTRICT HEATING SUPPLY LINES
[6 empty] | OD (DIMENSION) |  | 16
[6 empty] | VELOCITY |  | 0
FLEXALEN 600 |  | HEATING / COOLING (F / R) |  |  |  | VOLUMETRIC FLOW RATE |  | 0
[6 empty] | HEAT LOAD kW SOURCE |  | 0
[6 empty] | TEMP. DIFFERENCE (Tf - Tr) |  | 0
[6 empty] | USABLE TEMP. DIFF. |  | not appliable
SOURCE | 0 | RESERVE PRESSURE FOR PUMP |  |  |  | USABLE LOAD |  | not appliable
DELTA T |  | Temperature °C | Pressure loss bar | Dimension OD | END POINT | PRESSURE DROP FLOW |  | 0
NO | [5 empty] | PRESSURE DROP RETURN |  | 0
| FLOW | 0 | 0 | 16 |  | PRESSURE DROP TOTAL |  | 0
PUMP | 0 |  |  | #DIV/0!
0 | RETURN | 0 | 0 | not appliable |  | Pressure rating | at 95°C | 8
0 | not appliable |  |  | not appliable |  | max. Pressure | at Service Temperature | 16
|  | 0 |  |  |  | Pressure drop | FLEXALEN pipes only | 0
[6 empty] | Reserve press. | at Service Temperature | 16
[6 empty] | Soil temperature |  | 10
[6 empty] | Coverage |  | 800
[6 empty] | Lambda soil |  | 1
[6 empty] | Temperature drop Flow |  | #DIV/0!
[6 empty] | Trench Length |  | 0
[6 empty] | Dwell time Flow |  | #DIV/0!
[6 empty] | NET VOLUME |  | 0
NOTES:

## INSTRUCTION EN
All rights on the software are reserved for THERMAFLEX and HANS DRESLER, Wolfstal in Austria.
INSTRUCTION QuickCalc A-B (B-A) for FLEXALEN 600
Netcalculation module for EXCEL 97 and higher
The software QuickCalc A-B (B-A), in this instruction named "QuickCalc"
is designed for quick pipe sizing of FLEXALEN products for A to B connections.
Applications: Heating, Cooling, Potable water transportation.
If you have any question regarding this programm please sent an e-mail to the CoE Flexalen:
| CoE-Flexalen@thermaflex.com |  | or contact your local THERMAFLEX partner.
1.) | CALCULATION OF SINGLE PIPE SYSTEM = WATER TRANSPROT WITH ONE PIPE.
2.) | CALCULATION OF FLOW/RETURN PIPE SYSTEM = LINES WITH FLOW AND RETURN PIPES
3.) | POSSIBLE PARAMETER CHANGES IN THE PROGRAMME
4.) | PRINT OF THE CALCULATION
1.) CALCULATION OF SINGLE PIPE SYSTEM:
In our oppinion SINGLE LINES are preinsulated FLEXALEN-pipesystems, used for the transport of water from A to B.
For the calculation of the Temperature we expect that in ONE insualtion system ONE pipe is built in.
open the programme:
start EXCEL, open file "FLEXALEN_QuickCalc_600_v8_00.xls"
open sheet "CALC"
click on the button Supply line Button "O"
Then fill in ….
TEMPERATURE
Fill in the temperature of the medium in [°C]
TRENCH LENGTH
Fill in the Trench length in [m]
VOLUMETRIC FLOW
Fill in the quantity of the mdium im [l/s]
ADDITIONAL PRESSURE FOR THE PUMP
Fill in the needed raise of the pressure which then is added to pressure loss of the FLEXALN system.
(e.g. pressure required at the heat exchanger or indoor installation).
After ending the input the results are shown in the several spread sheet cells.
2.) CALCULATION OF FLOW/RETURN PIPE SYSTEM:
Under a FLOW/RETURN system we understand a preinsulated FLEXALEN-pipe system, built as an closed pipe system
with a flow and return line (heating systems)
We suggest that flow and return pipes are in one single insulation in the range of OD 25 to 63 mm OD and in two parallel pipes from OD 75 mm upwards.
open the programme:
start EXCEL, open file "FLEXALEN_QuickCalc_600_v8_00.xls"
open sheet "CALC"
click on the button Heating / Cooling Button "OO"
Then fill in ….
TEMPERATURE FLOW:
Fill in the flow temperature of the medium in [°C] at the boiler house
TEMPERATURE RETURN:
Fill in the return temperature of the medium in [°C] at the boiler house
TRENCH LENGTH
Fill in the Trench length in [m]
HEAT LOAD
Fill in the maximum heat load in [KW]
ADDITIONAL PRESSURE FOR THE PUMP
Fill in the needed raise of the pressure which then is added to pressure loss of the FLEXALEN system.
(e.g. Pressure for inhouse distribution or distribution in the boiler house).
After ending the input the results are shown in the several spread sheet cells.
3.) CHANGE PARAMETERS
For an adoption of the calculation some parameters can be changed, to reach as good as possible
the realistic situation in a network (e.g. to check an existing pipe network)
SIZE TUNING
in the sheet "CALC" you can fill in a factor to change the dimension [SIZE TUNING]
VALUES TO FILL IN Standard = 1
<1 | pipe size will decrease
1 | pipe size in standard
>1 | pipe size will increase
4.) PRINT OF THE CALCULATION
For printing the calculated results please select the sheet "printout" and select from the pulldownmenu "FILE" the button "print".
The following process is the standard excel print process.
INFORMATION:
The values are fixed on standard as following:
Temperature drop calculation:
Specifications for the calculation:
LAMBDA GROUND - Standard = 0,8 W/mK
TRENCH DEPTH ABOVE PIPE in mm - standard = 0,8 m
GROUND TEMPERATURE - standard = 10°C
The U - value used for the calculations are based on the following FLEXALEN products:
VS-RS40A16 |  | VS-R_125A2/25
VS-RS40A20 |  | VS-R_125A2/32
VS-R_90A25 |  | VS-R_160A2/40
VS-R_90A32 |  | VS-R_160A2/50
VS-R_90A40 |  | VS-R_200A2/63
VS-R_125A50
VS-R_125A63
VS-R_160A75
VS-R_160A90
VS-R200A110
FV-R200A125
FV-R225A140
FV-R250A160
FV-R315A225
A change of all these values is not possible in this software.
The outcome for the temperature drop calculation is just for orientation and not a precise value.
Legal remarks:
You are allowed to use ONE single copy of this programme on ONE computer.
The handing over of this software or parts of this software to a third party is strictly forbidden.
It is also strictly forbidden try to view the secured algorithm or other hidden parts of the software.
The handing over of the results of the calculation in form of the prepared print out is allowed.
The correctness of the given data is in your responisibility and is not connected to how the programm is working.
From side of THERMAFLEX or the developer of the programme we are excluding any responisbility
As this programme is designed for a very quick calculation in praxis, the main focus was set on
easy to use and praxis orientated values
If you put in extremely, not realistic lengths of the pipe the temperature loss will be displayed wrong.
All other values (pressure loss, maximum pressure,...) are displayed even in that case correct

## Release Info (hidden)
Flexalen QuickCalc
Flexalen 600
Date | Version | Changes
2010-02-03 | v8.00 (beta) | 1st multilingual language: english, german, bulgarian, dutch, Heatloss - temperature drop updated / new outlook,...
2010-02-09 | v8.00 (beta) | checked by several people and corrected

## Language (hidden)
INDEX | ENGLISH | GERMAN | BULAGRIAN | DUTCH | FRENCH | ROMANIAN | TURKISH | RUSSIAN | Russian
1 | PIPE SIZING FOR SINGLE OR DOUBLE LINES BETWEEN 2 NET POSITIONS | ROHRLEITUNGSBERECHNUNG - VERBINDUNG VON ZWEI NETZPUNKTEN MIT EINZEL- ODER DOPPELLEITUNG | ОРАЗМЕРЯВАНЕ НА ТРЪБОПРОВОД - СЪЕДИНЯВАНЕ НА 2 ТОЧКИ ЧРЕЗ ЕДНО- ИЛИ ДВУТРЪБНА СИСТЕМА | BUISAFMETING VOOR ENKEL OF DUBBEL LEIDING SYSTEEM VAN A NAAR B | DIMENSIONNEMENT TUBE FLEXALEN 600 LIGNE SIMPLE OU DOUBLE POUR LIAISON ENTRE BATIMENTS | DIMENSIONARE CONDUCTE CIRCUITE SIMPLE SAU DUBLE INTRE DOUA PUNCTE DIN RETEA | İKİ NOKTA ARASINDAKİ TEKLİ VEYA İKİLİ HATLAR İÇİN BORU EBADI | РАСЧЕТ ДИАМЕТРА ТРУБ ДЛЯ ОДНОТРУБНОЙ ИЛИ ДВУХТРУБНОЙ СИСТЕМ МЕЖДУ ДВУМЯ ТОЧКАМИ
2 | FLEXALEN 600 - PREINSULATED PIPE SYSTEMS | FLEXALEN 600 - ISOLIERTE ROHRSYSTEME | FLEXALEN 600 - СИСТЕМА ОТ ПРЕДВАРИТЕЛНО ИЗОЛИРАНИ ТРЪБИ | FLEXALEN 600 VOORGEISOLEERD LEIDINGSYSTEEM | FLEXALEN 600 - SYSTEME TUBES PRE-ISOLES | FLEXALEN 600-SISTEM CONDUCTE PREIZOLATE | FLEXALEN 600 - ÖNYALITIMLI BORU SİSTEMLERİ | FLEXALEN 600 - ПРЕДВАРИТЕЛЬНО ИЗОЛИРОВАННЫЕ ТРУБЫ
3 | MADE FOR DOMESTIC WATER DISTRIBUTION AND DISTRICT HEATING SUPPLY LINES | BERECHNUNG GILT FÜR WASSER IN LEITUNGSQUALITÄT UND FÜR NORMAL KONDITIONIERTES WASSER IN FERNWÄRMESYSTEMEN | ИЗЧИСЛЕНИЕТО Е ВАЛИДНО ЗА ПИТЕЙНА ВОДА И ЗА ВОДА ПРИГОДНА ЗА ОТОПЛИТЕЛНИ СИСТЕМИ | GESCHIKT VOOR TAPWATER EN WARMTE/KOUDE DISTRIBUTIE | CE PROGRAMME EST DEFINI POUR LE CALCUL DES RESEAUX DE CHAUFFAGE ET DE DISTRIBUTION D'EAU SANITAIRE | FABRICATE PENTRU RETELE DE DISTRIBUTIE A ENERGIEI TERMICE SI APEI MENAJERE | SICAK-SOĞUK SU TESİSATLARI VE BÖLGESEL ISITMA HATLARI İÇİN YAPILMIŞTIR | ЭТОТ РАСЧЕТ СДЕЛАН ДЛЯ СИСТЕМ БЫТОВОГО ВОДОСНАБЖЕНИЯ И ЦЕНТРАЛЬНОГО ОТОПЛЕНИЯ
4 | QUALITY FACTOR | QUALITÄTSFAKTOR | КАЧЕСТВЕН ФАКТОР | KWALITEIT FACTOR | FACT QUALITE | FACTOR CALITATE | KALİTE FAKTÖRÜ | КАЧЕСТВЕННЫЙ ФАКТОР
5 | TEMPERATUR FACTOR | TEMPERATURFAKTOR | ТЕМПЕРАТУРЕН ФАКТОР | TEMPERATUUR FACTOR | FACT TEMPERATURE | FACTOR TEMPERATURA | SICAKLIK FAKTÖRÜ | ТЕМПЕРАТУРНЫЙ ФАКТОР
6 | SIZE TUNING | ANPASSUNG DIMENSION | ДИМЕНЗИЯ ЗА НАПАСВАНЕ | OPTIMALISERINGS FACTOR | ADAPTATION DIAMETRE | OPTIMIZARE DIMENSIONARE | BOYUT AYARLAMA | ПОДБОР ДИАМЕТРА
7 | FLOW TEMPERATURE (Tf) | TEMPERATUR VORLAUF (Tf) | ТЕМПЕРАТУРА ПОДАВАНЕ | AANVOER TEMPERATUUR | TEMPERATURE DEPART | TEMPERATURA TUR | GİDİŞ SICAKLIĞI [°C] Tg | ТЕМПЕРАТУРА В "ПОДАЧЕ" (Tп)
8 | RETURN TEMPERATURE (Tr) | TEMPERATUR RÜCKLAUF (Tr) | ВЪЗВРАТЕНА ТЕМПЕРАТУРА | RETOUR TEMPERATUUR | TEMPERATURE RETOUR | TEMPERATURA RETUR | DÖNÜŞ SICAKLIĞI [°C] Td | ТЕМПЕРАТУРА В "ОБРАТКЕ" (То)
9 | TEMP. DIFFERENCE (Tf - Tr) | TEMP. SPREIZUNG (Tf - Tr) | ТЕРМОРАЗЛИКА (захр./връщ.) | TEMPERATUUR VERSCHIL | DELTA T (Td-Tr) | DIFERENTA TEMPERATURA | SICAKLIK FARKI (Tg - Td) | РАЗНИЦА ТЕМПЕРАТУР (Tп - Tо)
10 | TRENCH LENGTH | TRASSENLÄNGE | ДЪЛЖИНА НА ТРАСЕТО | TRACEE LENGTE | L.TRANCHEE(m) | LUNGIME SANT | TRANŞE(KANAL) UZUNLUĞU | ДЛИНА ТРАНШЕИ
11 | HEAT LOAD kW SOURCE | LEISTUNG kW QUELLE | ПОДАВАНА МОЩНОСТ | OVER TE BRENGEN VERMOGEN kW | PUISSANCE DEPART | PUTERE SURSA kW | ISI KAYNAĞI YÜKÜ ( KW ) | ТЕПЛОВАЯ НАГРУЗКА, кВт
12 | VOLUMETRIC FLOW RATE | MEDIUMMENGE | ДЕБИТ | VOLUMESTROOM | DEBIT | DEBIT VOLUMETRIC | HACİMSEL DEBİ | ОБЪЕМНЫЙ РАСХОД
13 | PIPE LENGTH | ROHRLÄNGE | ДЪЛЖИНА НА ТРЪБИТЕ | BUIS LENGTE | L.TUBES (m) | LUNGIME CONDUCTA | BORU UZUNLUĞU | ДЛИНА ТРУБ
14 | OD (DIMENSION) | DA (DIMENSION) | DA (външен диаметър на тръбата) | BUITEN DIAMETER | DIAMETRE EXT. | DE(DIMENSIUNE) | BORU DIŞ ÇAPI ÖLÇÜSÜ | Dнар. НАРУЖНЫЙ ДИАМЕТР
15 | VELOCITY | FLIESSGESCHWINDIGKEIT | СКОРОСТ НА ПОТОКА | SNELHEID | VITESSE | VITEZA | HIZ | СКОРОСТЬ ПОТОКА
16 | PRESSURE DROP FLOW | DRUCKVERLUST VORLAUF | ЗАГУБА НАЛЯГАНЕ / ПОДАВАНЕ | DRUKVERLIES AANVOER | PERTES CH. DEPART | PIERDERE PRESIUNE TUR | GİDİŞ HATTI BASINÇ KAYBI | ПОТЕРЯ ДАВЛЕНИЯ В "ПОДАЧЕ"
17 | PRESSURE DROP RETURN | DRUCKVERLUST RÜCKLAUF | ЗАГУБА НАЛЯГАНЕ / ВРЪЩАНЕ | DRUKVERLIES RETOUR | PERTES CH. RETOUR | PIERDERE PRESIUNE RETUR | DÖNÜŞ HATI BASINÇ KAYBI | ПОТЕРЯ ДАВЛЕНИЯ В "ОБРАТКЕ"
18 | PRESSURE DROP TOTAL | DRUCKVERLUST GESAMT | ЗАГУБА НАЛЯГАНЕ ОБЩО | DRUKVERLIES TOTAAL | PERTES CH. TOTALES | PIERDERE TOTALA PRESIUNE | TOPLAM BASINÇ KAYBI | ОБЩИЕ ПОТЕРИ ДАВЛЕНИЯ
19 | SUPPLY LINE (SINGLE LINE) | SANITÄR (EINROHRSYSTEM) | САНИТАРИЯ / БГВ | TOEVOERLEIDING | LIGNE SIMPLE | CIRCUIT ALIMENTARE (ACM) | BESLEME HATTI ( TEK HAT ) | ВОДОСНАБЖЕНИЕ (ОДНОТРУБНАЯ СИСТЕМА)
20 | HEATING / COOLING (F / R) | HEIZUNG / KÜHLUNG (VL / RL) | ОТОПЛЕНИЕ | VERWARMING / KOELING | ALLER+RETOUR | INCALZIRE/RACIRE(TUR-RETUR) | ISITMA / SOĞUTMA | ОТОПЛЕНИЕ (ДВУХТРУБНАЯ СИСТЕМА)
21 | USABLE TEMP. DIFF. | NUTZSPREIZUNG | ТЕРМОРАЗЛИКА | NUTTIG TEMPERATUURVERSCHIL | DELTA T UTILE | DIFERENTA TEMPERATURA UTILA | KULLANILIR SICAKLIK FARKI | РАЗНИЦА ТЕМПЕРАТУР В ТОЧКЕ 2
22 | USABLE LOAD | NUTZLAST | ПОЛЕЗЕН ТОВАР | NUTTIG VERMOGEN | PUISS UTILE | PUTERE UTILA | KULLANILIR ISI YÜKÜ | ДОСТАВЛЕННОЕ ТЕПЛО В ТОЧКЕ 2
23 | NET VOLUME | NETZVOLUMEN | ОБЕМ НА СИСТЕМАТА | NETTO VOLUME | VOL. RESEAU | VOLUM NET | NET HACİM | ОБЪЕМ СИСТЕМЫ
24 | SOURCE | QUELLE | ИЗТОЧНИК | BRON | DEPART | SURSA | KAYNAK | ИСТОЧНИК
25 | TEMP. DIFF. | SPREIZUNG | ТЕРМОРАЗЛИКА | TEMPERATUUR VERSCHIL | DELTA T | DIFERENTA TEMPERATURA | SICAKLIK FARKI | РАЗНИЦА ТЕМПЕРАТУР
26 | NO | OHNE | няма | NEE | 0 K | NU | HAYIR | НЕТ
27 | PUMP | PUMPE | ПОМПА | POMP | POMPE | POMPA | POMPA | НАСОС
28 | RESERVE PRESSURE FOR PUMP | VORDRUCK FÜR PUMPENAUSLEGUNG | ПРЕДПИСАНИЕ ЗА ИЗБОР НА ПОМПА | DRUKRESERVE VOOR POMP | PERTES CH. ADDITIONNELLES | REZERVA PRESIUNE POMPA | POMPA YEDEK BASINCI | ПОТЕРИ ДАВЛЕНИЯ ВО "ВНУТРЯНКЕ"
29 | Temperature °C | Temperatur °C | Температура °C | Temperatuur °C | Température °C | Temperatura °C | Sıcaklık °C | Температура °C
30 | Pressure loss bar | Druckverlust bar | Загуба на налягане bar | Drukverlies (bar) | Pertes ch. Lin. | Pierdere presiune bar | Basınç kaybı [bar] | Потери давления bar
31 | Dimension OD | Dimension DA | Размер на тръбата DA | Butien Diameter | Diamètre Ext | Diametru exterior | Boyut ( DIŞ ÇAP) | ДИАМЕТР Dнар.
32 | END POINT | END - PUNKT | ПОЛЕЗЕН ТОВАР | EIND PUNT | DESTINATION | PUNCT FINAL | SON NOKTA | КОНЕЧНАЯ ТОЧКА
33 | FLOW | VORLAUF | ПОДАВАНЕ | AANVOER | DEPART | TUR | GİDİŞ HATTI | "ПОДАЧА"
34 | RETURN | RÜCKLAUF | ВРЪЩАНЕ | RETOUR | RETOUR | RETUR | DÖNÜŞ HATTI | "ОБРАТКА"
35 | not appliable | entfällt | НЯМА | N.V.T. | Inapplicable | Neaplicabil | Uygulanamaz | не применяемо
36 | Soil temperature | Erdtemperatur | температура земя | Bodem Temperatuur | Température Sol | Temperatura sol | Toprak (zemin) sıcaklığı | Температура почвы
37 | Coverage | Überdeckung | дълб. на полагане | Sleuf Diepte | Prof.Tranch. | Adancime sant | Tranşe(kanal) derinliği | Глубина траншеи
38 | Lambda soil | Lambda Erde | Lambda земя | Warmte geleidingscoefficient Bodem | Lambda Sol | Lambda Sol | Toprak (zemin) ısı iletkenlik katsayısı | λ почвы
39 | Temperature drop Flow | Temperaturabfall VORLAUF | Темп.загуба ПОДАВАНЕ | Temperatuurverlies Aanvoer | Chute temp. ligne départ | Pierdere temperatura tur | Gidiş hattı sıcaklığı | Потери температуры в "подаче"
40 | Trench Length | Trassenlänge | Дължина на ТРАСЕТО | Tracee Lengte | Long.Tranch.m | Lungime sant | Tranşe (kanal) uzunluğu | Длина траншеи
41 | Dwell time Flow | Verweildauer VORLAUF | Времетраене на ПОТОКА | Verblijfstijd Stroming | Durée Ecoulement | DURATA PARCURS TUR | Akış süresi | Время подачи
42 | Pressure rating | Druckreihe | Налягане | Drukklasse | Press. Service | PRESIUNEA REGIM | Basınç değeri | Номинал. давление
43 | max. Pressure | Maximaldruck | Max налягане | Maximum Druk | Press. Max. | Presiune Max. | max.Basınç | Max. давление
44 | Pressure drop | Druckverlust | загуба налягане | Drukval | Pertes Chges. | Cadere Presiune | Basınç kaybı bar | Потери давления
45 | Reserve press. | Druckreserve | резерв налягане | Drukreserve | Réserve Press. | Rezerva presiune | statik basınç | Запас на потери давления во "внутрянке"
46 | at 95°C | bei 95°C | при 95°C | bij 95°C | à 95°C | la 95°C | 95°C de | при 95°C
47 | at Service Temperature | bei Anwendungstemperatur | при прилаганата темпер. | bij Bedrijfstemperatuur | à Température de Service | la Temperatura de lucru | İşletme sıcaklığında | при рабочей температуре
48 | FLEXALEN pipes only | im FLEXALEN Rohr | в тръбите | alleen voor FLEXALEN leidingen | Rés. FLEXALEN seul | Conducte Flexalen | Sadece FLEXALEN borular | Только в трубах FLEXALEN
49 | at Service Temperature | bei Anwendungstemperatur | при прилаганата темпер. | BIJ BEDRIJFSTEMPERATUUR | à Température de Service | la Temperatura de lucru | İşletme sıcaklığında | при рабочей температуре
50 | PLEASE CHOOSE APPLICATION: | BITTE ANWENDUNG WÄHLEN: | МОЛЯ ИЗБЕРЕТЕ ПРИЛОЖЕНИЕТО: | SELECTEER APPLICATIE: | CHOIX DE L'APPLICATION | VA RUGAM ALEGETI APLICATIA | LÜTFEN UYGULAMAYI SEÇİN: | ВЫБЕРИТЕ СИСТЕМУ:
51 | SUPPLY LINE → | SANITÄR → | САНИТАРИЯ / БГВ → | TOEVOERLEIDING → | LIGNE SIMPLE → | CIRCUIT A.C.M → | BESLEME HATTI ( TEK HAT ) → | ВОДОСНАБЖЕНИЕ →
52 | HEATING / COOLING → | HEIZUNG / KÜHLUNG → | ОТОПЛЕНИЕ → | VERWARMING / KOELING → | A/R CHAUF/EAU.GL → | INCALZIRE/RACIRE → | ISITMA / SOĞUTMA → | ОТОПЛЕНИЕ →
53 | Single pipe system: |  |  |  | Ligne Simple | SISTEM CONDUCTA SIMPLA | Tek Borulu Sistemler: | Обнотрубная система:
54 | TEMPERATURE | TEMPERATUR | Въведи температура в °C: | VUL DE TEMPERATUUR IN VAN HET MEDIUM | TEMPERATURE | TEMPERATURA | SICAKLIK | ТЕМПЕРАТУРА [°C]
55 | FILL IN TRENCH LENGTH | TRASSENLÄNGE | Въведи дължина на трасето в м: | VUL IN DE LENGTE VAN HET TRACEE | LONGUEUR DE TRANCHÉE | LUNGIME SANT | TRANŞE(KANAL) UZUNLUĞUNU GİR | ВВЕДИТЕ ДЛИНУ ТРАНШЕИ в [м]
56 | QUANTITY OF LIQUID | MEDIUMMENGE | Въведи дебит в л/сек: | HOEVEELHEID VLOEISTOF IN | DEBIT | DEBIT | AKIŞKANIN DEBİSİ | РАСХОД [литров/сек]
57 | ADDITIONAL PRESSURE FOR PUMP | VORDRUCK für PUMPE | Въведи налягане в крайна точка в bar: | ADDITIONELE PRUK VOOR DE POMP | Press. additionnelle à la pompe | PRESIUNE SUPLIMENTARA POMPA | POMPA İLAVE BASINCI | ПОТЕРИ ДАВЛЕНИЯ ВО "ВНУТРЯНКЕ" [bar]
58 | Twin line system: |  |  |  |  | Circuit dublu | Çift Hatlı(gidiş-dönüş) Sistemler: | Двухтрубная система:
59 | FLOW TEMPERATURE | TEMPERATUR VORLAUF | Въведи температура на подаване в °C: | VUL DE AANVOER TEMPERATUUR IN | TEMPERATURE DEPART en | TEMPERATURA TUR | AKIŞ SICAKLIĞI | ТЕМПЕРАТУРА В ПОДАЮЩЕМ ТРУБОПРОВОДЕ [°C]
60 | RETURN TEMPERATURE | TEMPERATUR RÜCKLAUF | Въведи възвратна температура в °C: | VUL DE RETOUR TEMPERATUUR IN | TEMPERATURE RETOUR en | TEMPERATURA RETUR | GERİ DÖNÜŞ SICAKLIĞI | ТЕМПЕРАТУРА В ОБРАТНОМ ТРУБОПРОВОДЕ [°C]
61 | TRENCH LENGTH | TRASSENLÄNGE | Въведи дължина на трасето в м: | VUL IN DE LENGTE VAN HET TRACEE | LONG.TRANCH. | LUNGIME SANT | TRANŞE(KANAL) UZUNLUĞU | ДЛИНА ТРАНШЕИ [м]
62 | HEAT LOAD | ÜBERTRAGENE LEISTUNG ab HEIZHAUS | Въведи мощност в крайна точка в kW: | VUL IN HET TE TRANSPORTEREN VERMOGEN IN | PUISSANCE | SARCINA TERMICA | ISI YÜKÜ | ТЕПЛОВАЯ НАГРУЗКА [кВт]
63 | ADDITIONAL PRESSURE FOR PUMP | VORDRUCK für PUMPE | Въведи налягане в крайна точка в bar: | ADDITIONELE PRUK VOOR DE POMP | PRESS. ADDITIONNELLE A LA POMPE | PRESIUNE SUPLIMENTARA POMPA | POMPA İLAVE BASINCI | ПОТЕРИ ДАВЛЕНИЯ ВО "ВНУТРЯНКЕ" [bar]
64
65 | °C | °C | °C | °C | °C | °C | °C | °C
66 | m | m | m | m | m | m | m | м
67 | l/s | l/s | l/s | l/s | l/s | l/s | lt/s | l/s
68 | bar | bar | bar | bar | bar | bar | bar | bar
69
70 | °C | °C | °C | °C | °C | °C | °C | °C
71 | °C | °C | °C | °C | °C | °C | °C | °C
72 | m | m | m | m | m | m | m | м
73 | kW | kW | kW | kW | kW | Kw | KW | кВт
74 | bar | bar | bar | bar | bar | bar | bar | bar
75
76
77
78
79
80
81
82
83
84
85
86
87
88
89
90
91
92
93
94
95
96
97
98
99
100

## PARAMETER_R (hidden)
QF | 1.83
TF | 1.03 |  | KUNSTSTOFFROHR |  | Pmax | 6
Mediumdichte | 0.98 |  | NR |  |  | 1.219
DRUCKVERLUSTE UND GRENZWERTE LAUT DATENBLATT | [8 empty] | DIMENSIONSFAKTOR
DRUCKVERLUSTTABELLE | [8 empty] | 1 | ENTSPRICHT
TYP | DI | PaT90/m | l/sec max | l/sec opt | L/sec min | v/min | V/max | V/optimal | AUSWAHL | Vmax
16 | 11.2 | 1122.4 | 0.088623 | 0.047266 | 0.0009847 | 0.01 | 0.9 | 0.48 | 0.01 | 0.9
20 | 14.4 | 826.2264 | 0.16278 | 0.10906 | 0.07 | 0.34 | 1 | 0.67 | 0.088623 | 1
25 | 20.4 | 540.383 | 0.35935 | 0.24011 | 0.11 | 0.37 | 1.1 | 0.735 | 0.16278 | 1.1
32 | 26 | 402.0563 | 0.63679 | 0.42718 | 0.21757 | 0.41 | 1.2 | 0.805 | 0.35935 | 1.2
40 | 32.6 | 305.1588 | 1.0845 | 0.72998 | 0.37542 | 0.45 | 1.3 | 0.875 | 0.63679 | 1.3
50 | 40.8 | 232.1357 | 1.8294 | 1.2414 | 0.65337 | 0.5 | 1.4 | 0.95 | 1.0845 | 1.4
63 | 51.4 | 175.1747 | 3.3183 | 2.2813 | 1.2444 | 0.6 | 1.6 | 1.1 | 1.8294 | 1.6
75 | 61.2 | 141.6069 | 5.2923 | 3.6017 | 1.9111 | 0.65 | 1.8 | 1.225 | 3.3183 | 1.8
90 | 73.6 | 113.0861 | 8.5046 | 5.8469 | 3.1892 | 0.75 | 2 | 1.375 | 5.2923 | 2
110 | 90 | 88.4933 | 14.6245 | 10.0146 | 5.4047 | 0.85 | 2.3 | 1.575 | 8.5046 | 2.3
125 | 102.2 | 75.7898 | 20.498 | 13.9386 | 7.3793 | 0.9 | 2.5 | 1.7 | 14.6245 | 2.5
140 | 114.4 | 66.0556 | 26.7113 | 18.4924 | 10.2736 | 1 | 2.6 | 1.8 | 20.498 | 2.6
160 | 130.8 | 56.1029 | 38.9478 | 26.8606 | 14.7733 | 1.1 | 2.9 | 2 | 26.7113 | 2.9
225 | 184 | 37.0096 | 95.6771 | 66.4424 | 37.2077 | 1.4 | 3.6 | 2.5 | 38.9478 | 3.6
D
TEMPERATUR VORLAUF |  | 0
TEMPERATUR RÜCKLAUF |  | 0
SPREIZUNG |  | 0
TRASSENLÄNGE |  | 0
LEISTUNG kW |  | 0
MEDIUMMENGE |  | 0
VORDRUCK für Pumpe |  | 0

## PARAMETER_T (hidden)
|  | Schaum DI | Schaum DA | Hüllrohr DI | HüllrohrDA |  |  | WE | 4196 |  | Material | Lambda
HÜLLROHR | 160 | 70 | 153 | 153 | 157 |  |  | s/H | 3600 |  | PB | 0.19
HÜLLROHR | 200 | 110 | 192 | 192 | 196 |  |  | Lambda Erde | 1 |  | PO | 0.04
STANGE | 110/125 |  |  | 190 | 200 |  |  | Verlegetiefe | 800 |  | HDPE | 0.43
STANGE | 140 |  |  | 214 | 225 |  |  | Erdtemperatur | 10 |  | PUR hart | 0.024
STANGE | 160 |  |  | 237.8 | 250
Verlegetiefe | 800 | [11 empty] | 1 pipe | 2 pipes |  | 1 pipe | 2 pipes
Material | W/(mK) | [6 empty] | OD | F600D | U [W/mK] | 1/2 U [W/mK] | F600-SLE | U [W/mK] | U [W/mK] | F600SM | U [W/mK] | U [W/mK]
Polybuten | 0.22 | [6 empty] | 16 | [6 empty] | VS-RS40A16 | 0.32299 | 0.55678
Luft ( innen ) | 15 | [6 empty] | 20 | [6 empty] | VS-RS40A20 | 0.33415 | 0.57789
PUR | 0.04 | [6 empty] | 25 | VS-R_125A2/25 | 0.30143 | 0.15071 | VS-R_90A25 | 0.1858 | 0.34433 | VS-R_50A25 | 0.35722 | 0.6158
Luft ( außen ) | 0.043 | [6 empty] | 32 | VS-R_125A2/32 | 0.37089 | 0.18545 | VS-R_90A32 | 0.22725 | 0.41434 | VS-R_63A32 | 0.38412 | 0.66012
HDPE | 0.43 | [6 empty] | 40 | VS-R_160A2/40 | 0.34058 | 0.17029 | VS-R_90A40 | 0.28416 | 0.5069 | VS-R_75A40
Lambda Erde | 1 | [6 empty] | 50 | VS-R_160A2/50 | 0.42717 | 0.21358 | VS-R_125A50 | 0.26128 | 0.4745 | VS-R_90A50
[8 empty] | 63 | VS-R_200A2/63 | 0.43162 | 0.21581 | VS-R_125A63 | 0.34417 | 0.60734
| MedDA | MedDI | 1/LAMDA-E | 1/LAMDA-D | W/(mk)-E | W/(mk)-D |  | 75 |  |  |  | VS-R_160A75 | 0.29319 | 0.52986
16-DE | 16 | 11.2 | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | 90 |  |  |  | VS-R_160A90 | 0.37214 | 0.65552
20-DE | 20 | 14.4 | #VALUE! | #VALUE! | #VALUE! | #VALUE! |  | 110 |  |  |  | VS-R200A110 | 0.36423 | 0.64785
25-DE | 25 | 20.4 | 5.5987 | 3.3873 | 0.139 | 0.114 |  | 125 |  |  |  | FV-R200A125 | 0.29363 | 0.5328
32-DE | 32 | 26 | 4.6196 | 4.1834 | 0.168 | 0.139 |  | 140 |  |  |  | FV-R225A140 | 0.29204 | 0.53194
40-D/E | 40 | 32.6 | 3.7295 | 3.8675 | 0.208 | 0.133 |  | 160 |  |  |  | FV-R250A160 | 0.31048 | 0.56411
50-D/E | 50 | 40.8 | 4.0634 | 5.0234 | 0.191 | 0.168 |  | 225 |  |  |  | FV-R315A225 | 0.30938 | 0.56774
63-E | 63 | 51.4 | 3.144 |  | 0.247 | 0.168
75-E | 75 | 61.2 | 3.4732 |  | 0.224 |  |  | Date: | 2010-02-03
90-E | 90 | 73.6 | 2.7462 |  | 0.283
110-ES | 110 | 90 | 2.8136 |  | 0.276
125-ES | 125 | 102.2 | 2.8222
140-ES | 140 | 114.4 | 2.8035
160-ES | 160 | 130.8 | 2.7863
E
E
PARAMETERTABELLE |  | 1.219 | single/double |  | 1 |  |  |  | 0.3
TYP | DI | PaT90/m | E | WmK-S | W/mK | v_min | v_max | v_optimal | W/mK D-D
16 | 11.2 | 1122.4 | E | 0.32299 | 0.32299 | 0.01 | 0.9 | 0.48 | 0
20 | 14.4 | 826.2264 | E | 0.33415 | 0.33415 | 0.34 | 1 | 0.67 | 0
25 | 20.4 | 540.383 | D | 0.15071 | 0.15071 | 0.37 | 1.1 | 0.735 | 3.75
32 | 26 | 402.0563 | D | 0.18545 | 0.18545 | 0.41 | 1.2 | 0.805 | 4.8
40 | 32.6 | 305.1588 | D | 0.17029 | 0.17029 | 0.45 | 1.3 | 0.875 | 6 |  | ARBEITSBEREICH enspricht rotem Bereich!!
50 | 40.8 | 232.1357 | D | 0.21358 | 0.21358 | 0.5 | 1.4 | 0.95 | 7.5
63 | 51.4 | 175.1747 | D | 0.21581 | 0.21581 | 0.6 | 1.6 | 1.1 | 9.45
75 | 61.2 | 141.6069 | E | 0.29319 | 0.29319 | 0.65 | 1.8 | 1.225 | 0
90 | 73.6 | 113.0861 | E | 0.37214 | 0.37214 | 0.75 | 2 | 1.375 | 0
110 | 90 | 88.4933 | E | 0.36423 | 0.36423 | 0.85 | 2.3 | 1.575 | 0
125 | 102.2 | 75.7898 | E | 0.29363 | 0.29363 | 0.9 | 2.5 | 1.7 | 0
140 | 114.4 | 66.0556 | E | 0.29204 | 0.29204 | 1 | 2.6 | 1.8 | 0
160 | 130.8 | 56.1029 | E | 0.31048 | 0.31048 | 1.1 | 2.9 | 2 | 0
225 | 184 | 37.0096 | E | 0.30938 | 0.30938 | 1.4 | 3.6 | 2.5 | 0
Note on D38: Bei Rohrsystemen, die im Bereich der kleineren Nenndurchmesser Doppelleitungen anbieten, kann durch die Eingabe von "D" bzw. "E" zwischen Doppelrohr- und Einzelrohrsystemen umgeschaltet werden.
Note on J5: Eingabe der Erdreichtemperatur. Diese Temperatur wird in Verlegetiefe mindest 10 m von der Rohrleitung entfernt mit einer Temperatursonde gemessen. Im Regelfall kann eine Temperatur von 10°C angenommen werden.

## TEMPERATUR (hidden)
CALCULATION TEMPERATURE DROP:
| OD | W/mK | W/m | W_pipe | V_t_sec | l/m | Volume
ROHR1 | 16 | 0.32299 | -3.2299 | 0 | #DIV/0! | 0.09852 | 0 | 0 | #DIV/0! | #DIV/0! | temp drop flow
ROHR2 | not appliable | #N/A | #N/A | #N/A | #DIV/0! | #N/A | #N/A | #N/A | #DIV/0! | #DIV/0! | temp drop return
[6 empty] | total volume: | 0
Temp diff |  |  | not appliable | #N/A
Quantity |  |  | 0 | #N/A
Usable load |  |  | #VALUE!
TEMPERATURE / PRESSURE RATING:
Pressure | Temperature
-15 | 16
0 | 16
20 | 16 | 20
40 | 15 | 20
60 | 12 | 10
70 | 10 | 10
80 | 9 | 15
95 | 8